## DiscreteAlarms
F ¦ Spare | Errors | wHMI_Fault1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on P.EMS front door | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency push button external ¦ 513S1ESTOP2 | Errors | wHMI_Fault1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on the container door (PCS room) | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Insulation Control Device PCS1 Alarm | Errors | wHMI_Fault1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Insulation losses occured TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Surge suppressor trip ¦ 001F1 | Errors | wHMI_Fault1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor intervention TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Main circuit breaker ¦ 003F2 | Errors | wHMI_Fault1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc Communication Equipment ¦ 301F1 | Errors | wHMI_Fault1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc Safety PLC cards ¦ 301F2 | Errors | wHMI_Fault1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ PCS 1 door open ¦ 527S1 | Errors | wHMI_Fault1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ PCS 2 door open ¦ 527S2 | Errors | wHMI_Fault1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Back AC door open PCS1 ¦ 527S3 | Errors | wHMI_Fault1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Back AC door open PCS1 ¦ 527S4 | Errors | wHMI_Fault1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Front Fan door open ¦ 527S6 | Errors | wHMI_Fault1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency State | Errors | wHMI_Fault1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency State Activated TROUBLESHOOTING Chech Emergency Alarm/Fault or reset Emergency Chain | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Master Profinet communication Error | Errors | wHMI_Fault2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Master Profinet comm. fault with PEMS Core TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Maximum Temperature Alarm PCS room | Errors | wHMI_Fault2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ PCS Sync Master-Slave Fault ¦ PEMS | Errors | wHMI_Fault2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Profisafe receive from Core Fault | Errors | wHMI_Fault2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Profisafe receive from EH05HD_1 Fault | Errors | wHMI_Fault2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Profisafe receive from EH05HD_2 Fault | Errors | wHMI_Fault2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply PCS1 ¦ 013F2 | Errors | wHMI_Alarm1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply PCS2 ¦ 013F3 | Errors | wHMI_Alarm1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Main circuit breaker UPS ¦ 101F2 | Errors | wHMI_Alarm1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Surge suppressor UPS trip ¦ 101F3 | Errors | wHMI_Alarm1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor intervention TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PS unit 1 24Vdc open ¦ 107F2+107T1 | Errors | wHMI_Alarm1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PS unit 2 24Vdc open ¦ 107F3+107T2 | Errors | wHMI_Alarm1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply UPS PCS1 ¦ 107F4 | Errors | wHMI_Alarm1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply UPS PCS2¦ 107F5 | Errors | wHMI_Alarm1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc digital PLC cards ¦ 301F3 | Errors | wHMI_Alarm1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc analog PLC cards ¦ 301F4 | Errors | wHMI_Alarm1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PLC IO internal ¦ 301F5 | Errors | wHMI_Alarm1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PLC IO external ¦ 301F6 | Errors | wHMI_Alarm1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PCS Signals ¦ 301F7 | Errors | wHMI_Alarm1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply fan 1 ¦ 011F1 | Errors | wHMI_Alarm2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply fan 2 ¦ 011F2 | Errors | wHMI_Alarm2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Internal intake pressure switch | Errors | wHMI_Alarm2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ External intake pressure switch | Errors | wHMI_Alarm2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Irresponsive fan 1 | Errors | wHMI_Alarm2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Irresponsive fan 2 | Errors | wHMI_Alarm2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ EH05HD1 Profinet communication Error | Errors | wHMI_Alarm3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ EH05HD2 Profinet communication Error | Errors | wHMI_Alarm3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL1, PCS1 CAN communication Error | Errors | wHMI_Alarm3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL2, PCS1 CAN communication Error | Errors | wHMI_Alarm3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL1, PCS2 CAN communication Error | Errors | wHMI_Alarm3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL2, PCS2 CAN communication Error | Errors | wHMI_Alarm3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 1 in Alarm | Errors | wHMI_Alarm3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 1 in Fault State TROUBLESHOOTING Check State Machine 1 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 2 in Alarm | Errors | wHMI_Alarm3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 2 in Fault State TROUBLESHOOTING Check State Machine 2 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 3 in Alarm | Errors | wHMI_Alarm3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 3 in Fault State TROUBLESHOOTING Check State Machine 3 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 4 in Alarm | Errors | wHMI_Alarm3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 4 in Fault State TROUBLESHOOTING Check State Machine 4 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS1 shot | Errors | wHMI_Alarm3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS2 shot | Errors | wHMI_Alarm3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency State Activated TROUBLESHOOTING Chech Emergency Alarm/Fault or reset Emergency Chain | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 1 high temperature ¦ 561B1 | Warnings | wHMI_Warning1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 1 low temperature ¦ 561B1 | Warnings | wHMI_Warning1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 1 temperature read fail ¦ 561B1 | Warnings | wHMI_Warning1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 1 high humidity ¦ 561B1 | Warnings | wHMI_Warning1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 1 low humidity ¦ 561B1 | Warnings | wHMI_Warning1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 1 humidity read fail ¦ 561B1 | Warnings | wHMI_Warning1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 2 high temperature ¦ 561B2 | Warnings | wHMI_Warning1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the C-BESSHD room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 2 low temperature ¦ 561B2 | Warnings | wHMI_Warning1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 2 temperature read fail ¦ 561B2 | Warnings | wHMI_Warning1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 2 high humidity ¦ 561B2 | Warnings | wHMI_Warning1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 2 low humidity ¦ 561B2 | Warnings | wHMI_Warning1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS room sensor 2 humidity read fail ¦ 561B2 | Warnings | wHMI_Warning1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Front PEMS door open ¦ 527S5 | Warnings | wHMI_Warning2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PEMS or fans room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Insulation Control Device PCS1 Prewarning | Warnings | wHMI_Warning2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Insulation losses occured TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS1 CL1 Synch Warning | Warnings | wHMI_Warning3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS1 CL2 Synch Warning | Warnings | wHMI_Warning3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS2 CL1 Synch Warning | Warnings | wHMI_Warning3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS2 CL2 Synch Warning | Warnings | wHMI_Warning3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: No Master | Warnings | wHMI_Warning3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: More than one Master | Warnings | wHMI_Warning3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: Slave Error | Warnings | wHMI_Warning3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ PCS Synch Warning: No Sync Active | Warnings | wHMI_Warning3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN HVAC unit not Enabled TROUBLESHOOTING Check the status of the HVAC, in case enable it | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Both HVAC compressor Disabled TROUBLESHOOTING Check the status of the HVAC, in case enable it | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor PCS1 open | Warnings | wHMI_Warning3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
| Warnings | wHMI_Warning3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0

## Sheet1
F ¦ Spare | F ¦ Spare | ok
F ¦ Emergency push button external ¦ 513S1ESTOP2 | F ¦ Emergency push button external ¦ 513S1ESTOP2 | ok
F ¦ Insulation Control Device PCS1 Alarm | F ¦ Insulation Control Device PCS1 Alarm ¦ | ok
F ¦ Surge suppressor trip ¦ 001F1 | F ¦ Surge suppressor trip ¦ 001F1 | ok
F ¦ Main circuit breaker ¦ 003F2 | F ¦ Main circuit breaker ¦ 003F2 | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Power supply 24Vdc Communication Equipment ¦ 301F1 | F ¦ Power supply 24Vdc Communication Equipment ¦ 301F1 | ok
F ¦ Power supply 24Vdc Safety PLC cards ¦ 301F2 | F ¦ Power supply 24Vdc Safety PLC cards ¦ 301F2 | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ PCS 1 door open ¦ 527S1 | F ¦ PCS 1 door open ¦ 527S1 | ok
F ¦ PCS 2 door open ¦ 527S2 | F ¦ PCS 2 door open ¦ 527S2 | ok
F ¦ Back AC door open PCS1 ¦ 527S3 | F ¦ Back AC door open PCS1 ¦ 527S3 | ok
F ¦ Back AC door open PCS1 ¦ 527S4 | F ¦ Back AC door open PCS1 ¦ 527S4 | ok
F ¦ Front Fan door open ¦ 527S6 | F ¦ Front Fan door open ¦ 527S6 | ok
F ¦ Emergency State | F ¦ Emergency State ¦ | ok
F ¦ Master Profinet communication Error | F ¦ Master Profinet communication Error ¦ | ok
F ¦ Maximum Temperature Alarm PCS room | F ¦ Maximum Temperature Alarm PCS room¦ | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ PCS Sync Master-Slave Fault ¦ PEMS | F ¦ Spare | not ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Spare | F ¦ Spare | ok
F ¦ Profisafe receive from Core Fault | F ¦ Profisafe receive from Core Fault | ok
F ¦ Profisafe receive from EH05HD_1 Fault | F ¦ Profisafe receive from EH05HD_1 Fault | ok
F ¦ Profisafe receive from EH05HD_2 Fault | F ¦ Profisafe receive from EH05HD_2 Fault | ok
A ¦ Power supply PCS1 ¦ 013F2 | A ¦ Power supply PCS1 ¦ 013F2 | ok
A ¦ Power supply PCS2 ¦ 013F3 | A ¦ Power supply PCS2 ¦ 013F3 | ok
A ¦ Main circuit breaker UPS ¦ 101F2 | A ¦ Main circuit breaker UPS ¦ 101F2 | ok
A ¦ Surge suppressor UPS trip ¦ 101F3 | A ¦ Surge suppressor UPS trip ¦ 101F3 | ok
A ¦ Power Supply UPS PS unit 1 24Vdc open ¦ 107F2+107T1 | A ¦ Power Supply UPS PS unit 1 24Vdc open ¦ 107F2+107T1 | ok
A ¦ Power Supply UPS PS unit 2 24Vdc open ¦ 107F3+107T2 | A ¦ Power Supply UPS PS unit 2 24Vdc open ¦ 107F3+107T2 | ok
A ¦ Power supply UPS PCS1 ¦ 107F4 | A ¦ Power supply UPS PCS1 ¦ 107F4 | ok
A ¦ Power supply UPS PCS2¦ 107F5 | A ¦ Power supply UPS PCS2¦ 107F5 | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Power supply 24Vdc digital PLC cards ¦ 301F3 | A ¦ Power supply 24Vdc digital PLC cards ¦ 301F3 | ok
A ¦ Power supply 24Vdc analog PLC cards ¦ 301F4 | A ¦ Power supply 24Vdc analog PLC cards ¦ 301F4 | ok
A ¦ Power supply 24Vdc PLC IO internal ¦ 301F5 | A ¦ Power supply 24Vdc PLC IO internal ¦ 301F5 | ok
A ¦ Power supply 24Vdc PLC IO external ¦ 301F6 | A ¦ Power supply 24Vdc PLC IO external ¦ 301F6 | ok
A ¦ Power supply 24Vdc PCS Signals ¦ 301F7 | A ¦ Power supply 24Vdc PCS Signals ¦ 301F7 | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Power supply fan 1 ¦ 011F1 | A ¦ Power supply fan 1 ¦ 011F1 | ok
A ¦ Power supply fan 2 ¦ 011F2 | A ¦ Power supply fan 2 ¦ 011F2 | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Internal intake pressure switch | A ¦ Internal intake pressure switch ¦ | ok
A ¦ External intake pressure switch | A ¦ External intake pressure switch ¦ | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Irresponsive fan 1 | A ¦ Irresponsive fan 1 ¦ | ok
A ¦ Irresponsive fan 2 | A ¦ Irresponsive fan 2 ¦ | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ EH05HD1 Profinet communication Error | A ¦ EH05HD1 Profinet communication Error ¦ | ok
A ¦ EH05HD2 Profinet communication Error | A ¦ EH05HD2 Profinet communication Error ¦ | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ CL1, PCS1 CAN communication Error | A ¦ CL1,PCS1 CAN communication Error ¦ | not ok
A ¦ CL2, PCS1 CAN communication Error | A ¦ CL2,PCS1 CAN communication Error ¦ | not ok
A ¦ CL1, PCS2 CAN communication Error | A ¦ CL1,PCS2 CAN communication Error ¦ | not ok
A ¦ CL2, PCS2 CAN communication Error | A ¦ CL2,PCS2 CAN communication Error ¦ | not ok
A ¦ State Machine 1 in Alarm | A ¦ State Machine 1 in Alarm ¦ | ok
A ¦ State Machine 2 in Alarm | A ¦ State Machine 2 in Alarm ¦ | ok
A ¦ State Machine 3 in Alarm | A ¦ State Machine 3 in Alarm ¦ | ok
A ¦ State Machine 4 in Alarm | A ¦ State Machine 4 in Alarm ¦ | ok
A ¦ Spare | A ¦ Spare | ok
A ¦ Spare | A ¦ Spare | ok
W ¦ Surge Suppressor PCS1 shot | W ¦ Surge Suppressor PCS1 shot ¦ | ok
W ¦ Surge Suppressor PCS2 shot | W ¦ Surge Suppressor PCS2 shot ¦ | ok
W ¦ PCS room sensor 1 high temperature ¦ 561B1 | W ¦ PCS room sensor 1 high temperature ¦ 561B1 | ok
W ¦ PCS room sensor 1 low temperature ¦ 561B1 | W ¦ PCS room sensor 1 low temperature ¦ 561B1 | ok
W ¦ PCS room sensor 1 temperature read fail ¦ 561B1 | W ¦ PCS room sensor 1 temperature read fail ¦ 561B1 | ok
W ¦ PCS room sensor 1 high humidity ¦ 561B1 | W ¦ PCS room sensor 1 high humidity ¦ 561B1 | ok
W ¦ PCS room sensor 1 low humidity ¦ 561B1 | W ¦ PCS room sensor 1 low humidity ¦ 561B1 | ok
W ¦ PCS room sensor 1 humidity read fail ¦ 561B1 | W ¦ PCS room sensor 1 humidity read fail ¦ 561B1 | ok
W ¦ PCS room sensor 2 high temperature ¦ 561B2 | W ¦ PCS room sensor 2 high temperature ¦ 561B2 | ok
W ¦ PCS room sensor 2 low temperature ¦ 561B2 | W ¦ PCS room sensor 2 low temperature ¦ 561B2 | ok
W ¦ PCS room sensor 2 temperature read fail ¦ 561B2 | W ¦ PCS room sensor 2 temperature read fail ¦ 561B2 | ok
W ¦ PCS room sensor 2 high humidity ¦ 561B2 | W ¦ PCS room sensor 2 high humidity ¦ 561B2 | ok
W ¦ PCS room sensor 2 low humidity ¦ 561B2 | W ¦ PCS room sensor 2 low humidity ¦ 561B2 | ok
W ¦ PCS room sensor 2 humidity read fail ¦ 561B2 | W ¦ PCS room sensor 2 humidity read fail ¦ 561B2 | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Front PEMS door open ¦ 527S5 | W ¦ Front PEMS door open ¦ 527S5 | ok
W ¦ Insulation Control Device PCS1 Prewarning | W ¦ Insulation Control Device PCS1 Prewarning ¦ | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ PCS1 CL1 Synch Warning | W ¦ PCS1 CL1 Synch Warning ¦ | ok
W ¦ PCS1 CL2 Synch Warning | W ¦ PCS1 CL2 Synch Warning ¦ | ok
W ¦ PCS2 CL1 Synch Warning | W ¦ PCS2 CL1 Synch Warning ¦ | ok
W ¦ PCS2 CL2 Synch Warning | W ¦ PCS2 CL2 Synch Warning ¦ | ok
W ¦ PCS Synch Warning: No Master | W ¦ PCS Synch Warning: No Master¦ | ok
W ¦ PCS Synch Warning: More than one Master | W ¦ PCS Synch Warning: More than one Master¦ | ok
W ¦ PCS Synch Warning: Slave Error | W ¦ PCS Synch Warning: Slave Error¦ | ok
W ¦ PCS Synch Warning: No Sync Active | W ¦ PCS Synch Warning: No Sync Active¦ | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Spare | W ¦ Spare | ok
W ¦ Surge Suppressor PCS1 open | W ¦ Surge Suppressor PCS1 open ¦ | ok
| W ¦ Surge Suppressor PCS2 open ¦ | ok