## Foglio1
W | [Partial Operation] Notice | Warnings | BB.wWarn1St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. TROUBLESHOOTING Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [Partial Operation] Alarm | Warnings | BB.wWarn1St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. TROUBLESHOOTING Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [Partial Operation] System Stop | Warnings | BB.wWarn1St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. TROUBLESHOOTING Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] Partial Operation | Warnings | BB.wWarn1St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. TROUBLESHOOTING Refer to "Partial Operation" of [Function Description] to find more about detailed function and operation. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] Protection | Warnings | BB.wWarn1St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "E-Stop' of [Function Description] to find more about [E-Stop] functions. TROUBLESHOOTING Refer to "E-Stop' of [Function Description] to find more about [E-Stop] functions. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] SPD | Warnings | BB.wWarn1St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "E-Stop' of [Function Description] to find more about [E-Stop] functions. TROUBLESHOOTING Refer to "E-Stop' of [Function Description] to find more about [E-Stop] functions. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] Permanent Protection | Warnings | BB.wWarn1St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Refer to "E-Stop' of [Function Description] to find more about [E-Stop] functions. TROUBLESHOOTING Refer to "E-Stop' of [Function Description] to find more about [E-Stop] functions. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] Fire Detection (Internal) | Warnings | BB.wWarn1St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] Fire Detection (External) | Warnings | BB.wWarn1St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [E-Stop] FFS Trouble | Warnings | BB.wWarn1St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wWarn1St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wWarn1St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wWarn1St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wWarn1St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [DS Operation] Trip | Warnings | BB.wWarn1St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Disconnection switch trip (0x004A Sys. Alarm #1 Bit 14) TROUBLESHOOTING - | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | [Initialize] Need Commissioning | Warnings | BB.wWarn1St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN [Initialize] Need Commissioning is set when necessary operational setting is uncompleted. "Writing command" cannot be perfomed, TROUBLESHOOTING Shows that product operational setting is uncompleted. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect RTU Alarm | Warnings | BB.wWarn2St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect RTU Protection | Warnings | BB.wWarn2St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect TCP#1 Alarm | Warnings | BB.wWarn2St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN When a function to check on a lost TCPIP Port#1 comm. is set. When comm. is lost during the alarm set time. (0x004B Sys. Alarm #2 Bit 2) TROUBLESHOOTING When a function to check on TCPIP comm. between the upper Sys. and Sys. BMS is set. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect TCP#1 Protection | Warnings | BB.wWarn2St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN When a function to check on a lost TCPIP Port#1 comm. is set. When comm. is lost during the protection set time. TROUBLESHOOTING When a function to check on TCPIP comm. between the upper Sys. and Sys. BMS is set. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect TCP#2 Alarm | Warnings | BB.wWarn2St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN When a function to check on a lost TCPIP Port#2 comm. is set. When comm. is lost during the alarm set time. (0x004B Sys. Alarm #2 Bit 4) TROUBLESHOOTING When a function to check on TCPIP comm. between the upper Sys. and Sys. BMS is set. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect TCP#2 Protection | Warnings | BB.wWarn2St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN When a function to check on a lost TCPIP Port#2 comm. is set. When comm. is lost during the protection set time. TROUBLESHOOTING When a function to check on TCPIP comm. between the upper Sys. and Sys. BMS is set. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect TCP#3 Alarm | Warnings | BB.wWarn2St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN When a function to check on a lost TCPIP Port#3 comm. is set. When comm. is lost during the alarm set time. (0x004B Sys. Alarm #2 Bit 6) TROUBLESHOOTING When a function to check on TCPIP comm. between the upper Sys. and Sys. BMS is set. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Disconnect TCP#3 Protection | Warnings | BB.wWarn2St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN When a function to check on a lost TCPIP Port#3 comm. is set. When comm. is lost during the protection set time. TROUBLESHOOTING When a function to check on TCPIP comm. between the upper Sys. and Sys. BMS is set. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wWarn2St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wWarn2St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Over CCL Alarm | Warnings | BB.wWarn2St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | FFS Smoke Detection Alarm | Warnings | BB.wWarn2St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | SOC Upper Limit Setting Alarm | Warnings | BB.wWarn2St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | String SOC Imbalance | Warnings | BB.wWarn2St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Set: difference between "Service SOC (Connected) (Maximum)" and "Service SOC (Connected) (Minimum)" is 10.0% or more. Reset: difference between "Service SOC (Connected) (Maximum)" and "Service SOC (Connected) (Minimum)" is less than 5.0%. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | String Count Imbalance | Warnings | BB.wWarn2St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN String Count Imbalance is set when number of string set at Sys. BMS is not identical to sum of number of string set at each rack connected to Sys. BMS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack Count Imbalance | Warnings | BB.wWarn2St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN The number of racks connected to Sys. BMS is higher than that of racks set at Sys. BMS. (0x004B Sys. Alarm #2 Bit 15) TROUBLESHOOTING When the operation specification set at Sys. is not identical to the installed operation specification. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #1(string#1(+)) sensing fail. | Warnings | BB.wBRWarnCom1St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #1(string#1(+)) sensing fail. (0x004C RackComAlm #1 sum. Bit 0) TROUBLESHOOTING 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #2(string#2(+)) sensing fail. | Warnings | BB.wBRWarnCom1St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #3(main(-)) sensing fail. | Warnings | BB.wBRWarnCom1St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #3(main(-)) sensing fail. (0x004C RackComAlm #1 sum. Bit 2) TROUBLESHOOTING 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #1(string#1(+)) open fail. | Warnings | BB.wBRWarnCom1St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #1(string#1(+)) open fail. (0x004C RackComAlm #1 sum. Bit 3) TROUBLESHOOTING 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #2(string#2(+)) open fail. | Warnings | BB.wBRWarnCom1St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #3(main(-)) open fail. | Warnings | BB.wBRWarnCom1St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #3(main(-)) open fail. (0x004C RackComAlm #1 sum. Bit 5) TROUBLESHOOTING 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> system communication fail. | Warnings | BB.wBRWarnCom1St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> Sys. comm. fail. No comm. for 30s. (0x004C RackComAlm #1 sum. Bit 6) TROUBLESHOOTING 1. Check | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | String current imbalance. | Warnings | BB.wBRWarnCom1St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN string current imbalance. (0x004C RackComAlm #1 sum. Bit 7) TROUBLESHOOTING When one alarm bit or more is set in common areas of all racks connected to Sys. BMS, the alarm bit is set at alarm sum.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fuse #1(string#1(+)) life fail. | Warnings | BB.wBRWarnCom1St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fuse #1(string#1(+)) life fail. (0x004C RackComAlm #1 sum. Bit 8) TROUBLESHOOTING 1. Check fuse status 2. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fuse #2(string#2(+)) life fail. | Warnings | BB.wBRWarnCom1St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fuse #3(main(-)) life fail. | Warnings | BB.wBRWarnCom1St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fuse #3(main(-)) life fail. (0x004C RackComAlm #1 sum. Bit 10) TROUBLESHOOTING 1. Check fuse status 2. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #1(string#1(+)) life fail. | Warnings | BB.wBRWarnCom1St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #1(string#1(+)) life fail. TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #2(string#2(+)) life fail. | Warnings | BB.wBRWarnCom1St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Dc contactor #3(main(-)) life fail. | Warnings | BB.wBRWarnCom1St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #3(main(-)) life fail TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | String voltage imbalance. | Warnings | BB.wBRWarnCom1St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN String voltage imbalance TROUBLESHOOTING [RackComAlm sum.] When one alarm bit or more is set in common areas of all racks connected to Sys. BMS, the alarm bit is set at alarm sum.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack pcb over temperature. | Warnings | BB.wBRWarnCom1St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Rack pcb over temperature (0x004C RackComAlm #1 sum. Bit 15) TROUBLESHOOTING 1. Check the environmental condition (HVAC.. ) 2. Read Min/Max cell temperature → Check BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | User protection enable | Warnings | BB.wBRWarnCom2St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN user protection enable TROUBLESHOOTING [RackComAlm sum.] When one alarm bit or more is set in common areas of all racks connected to Sys. BMS, the alarm bit is set at alarm sum.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarnCom2St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #1(string#1(+)) sensing fail. | Errors | BB.wBRFltCom1St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #1(string#1(+)) sensing fail. dcsw (+) cmd ≠ dcsw (+) sensor status for 3s TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #2(string#2(+)) sensing fail. | Errors | BB.wBRFltCom1St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #3(main(-)) sensing fail. | Errors | BB.wBRFltCom1St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #3(main(-)) sensing fail. dcsw (-) cmd ≠ dcsw (-) sensor status for 3s TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #1(string#1(+)) open fail. | Errors | BB.wBRFltCom1St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #1(string#1(+)) open fail. DC Switch(+) Open && ¦String Current¦ ≥ 600mA TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #2(string#2(+)) open fail. | Errors | BB.wBRFltCom1St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #3(main(-)) open fail. | Errors | BB.wBRFltCom1St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #3(main(-)) open fail. DC Switch(-) Open && ¦String Current¦ ≥ 600mA TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> system communication fail. | Errors | BB.wBRFltCom1St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> Sys. comm. fail. No comm. for 30s. TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | String current imbalance. | Errors | BB.wBRFltCom1St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN string current imbalance. TROUBLESHOOTING [Rack Common Protection sum.] When one protection bit or more is set in common areas of all racks connected to Sys. BMS, the protectin bit is set at protection sum.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fuse #1(string#1(+)) life fail. | Errors | BB.wBRFltCom1St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fuse #1(string#1(+)) life fail. Fuse (+) Blown (Micro Switch Close). TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. 1. Check fuse status 2. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fuse #2(string#2(+)) life fail. | Errors | BB.wBRFltCom1St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fuse #3(main(-)) life fail. | Errors | BB.wBRFltCom1St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fuse #3(main(-)) life fail. Fuse (-) Blown (Micro Switch Close). TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. 1. Check fuse status 2. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #1(string#1(+)) life fail. | Errors | BB.wBRFltCom1St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #1(string#1(+)) life fail. TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #2(string#2(+)) life fail. | Errors | BB.wBRFltCom1St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Dc contactor #3(main(-)) life fail. | Errors | BB.wBRFltCom1St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN dc contactor #3(main#1(-)) life fail. 'TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack. 1. Replace the DC contactor or Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | String voltage imbalance. | Errors | BB.wBRFltCom1St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN String voltage imbalance TROUBLESHOOTING [Rack Common Protection sum.] When one protection bit or more is set in common areas of all racks connected to Sys. BMS, the protectin bit is set at protection sum.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack pcb over temperature. | Errors | BB.wBRFltCom1St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Rack over temperature > 85°C for 5s TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after Sys. has cooled down | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | User protection enable | Errors | BB.wBRFltCom2St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN user protection enable TROUBLESHOOTING [Rack Common Protection sum.] When one protection bit or more is set in common areas of all racks connected to Sys. BMS, the protectin bit is set at protection sum.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFltCom2St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell over voltage. | Warnings | BB.wBRWarn1St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell over voltage Max Cell Voltage ≥ 4.19V for 1 S TROUBLESHOOTING Stop discharging and check status. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell under voltage. | Warnings | BB.wBRWarn1St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell under voltage Min Cell Voltage ≤ 2.8V for 1 S TROUBLESHOOTING Stop discharging and check status. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack cell voltage imbalance. | Warnings | BB.wBRWarn1St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell voltage imbalance SOC ≥ 10% && Cell Voltage △ ≥ 200mV for 5 S TROUBLESHOOTING Stop operation and check the battery Sys.. Check the rack when available. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell voltage hold. | Warnings | BB.wBRWarn1St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell voltage hold Cell Voltage' = Cell Voltage for 1800 s TROUBLESHOOTING Stop operation and check the battery Sys.. Reduce power as ratio of Normal/Total Rack. Check the rack when available. 1. Check Module BMS 2. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell over temperature. | Warnings | BB.wBRWarn1St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell over temperature Max Cell Temperature > 60°C for 3s TROUBLESHOOTING Reduced power to 50%. Reduce discharging power : -> Rating power * (Normal Rack / Total Rack) | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell under temperature. | Warnings | BB.wBRWarn1St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell under temperature Max Cell Temperature < -10°C for 5s TROUBLESHOOTING Check the battery when available Check the failed Rack 1. Check the environmental condition (HVAC.. ) 2. Read Min/Max cell temperature → Check BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell temperature imbalance. | Warnings | BB.wBRWarn1St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell temperature imbalance cell temperature difference > 15°C per 30s TROUBLESHOOTING Stop operation and check the battery Sys.. Check the rack&module when available. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn1St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Iterative Cell Balancing | Warnings | BB.wBRWarn1St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN iterative cell balancing TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module open wire detection. | Warnings | BB.wBRWarn1St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Recurring the cell over voltage. | Warnings | BB.wBRWarn1St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Cell deviation fail | Warnings | BB.wBRWarn1St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module cell voltage imbalance | Warnings | BB.wBRWarn1St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn1St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn1St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn1St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module voltage difference. | Warnings | BB.wBRWarn2St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN module voltage difference ¦Module Block V - Module Cell Sum V¦ ≥ 2.4V for 3 S TROUBLESHOOTING Check the module when available | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> module communication fail #1. | Warnings | BB.wBRWarn2St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #1. RX Address ≠ Module Count for 10 S TROUBLESHOOTING Stop operation and check the battery Sys.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> module communication fail #2. | Warnings | BB.wBRWarn2St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #2. Scan Fail for 10 S TROUBLESHOOTING Stop operation and check the battery Sys.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> module communication fail #3. | Warnings | BB.wBRWarn2St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #3. TX Command ≠ RX Command for 10 S TROUBLESHOOTING Stop operation and check the battery Sys.. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | All module sleep. | Warnings | BB.wBRWarn2St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN all module sleep Min Cell Voltage ≤ 2.5V for 7200 S TROUBLESHOOTING Check the rack&module when available. Report it to SDI representatives and investigate the module in detail. 1. Check the power connection 2. Check the rack & module voltage | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Afe(module bms) hardware fail #1 | Warnings | BB.wBRWarn2St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN afe(module bms) hardware fail #1 ALRTRST Bit Set & Module ID = 0 for 10 times TROUBLESHOOTING Stop operation and check the battery Sys.. Reduce power as ratio of Normal/Total Rack. Check the rack when available. 1. Check and replace Rack BMS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module pcb over temperature. | Warnings | BB.wBRWarn2St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN module mount check TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module pcb under temperature. | Warnings | BB.wBRWarn2St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN module pcb under temperature. (0x0051 Rack String Alarm #2 sum. Bit 7) TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> module communication fail #4. | Warnings | BB.wBRWarn2St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #4. Data Fail for 10 S TROUBLESHOOTING Stop operation and check the battery Sys.. Reduce power as ratio of Normal/Total Rack. Check the rack when available. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Afe(module bms) hardware fail #2 | Warnings | BB.wBRWarn2St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN afe(module bms) hardware fail #2 ALRTTEMP Bit Set for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. Reduce power as ratio of Normal/Total Rack. Check the rack when available. 1. Check and replace Rack BMS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Afe(module bms) hardware fail #3 | Warnings | BB.wBRWarn2St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN afe(module bms) hardware fail #3 ALRTHVUV or ALRTHVHDRM Bit Set for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. Reduce power as ratio of Normal/Total Rack. Check the rack when available. 1. Check and replace Rack BMS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fire detect condition #1. | Warnings | BB.wBRWarn2St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fire detect condition #2. | Warnings | BB.wBRWarn2St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fire detect condition #3. | Warnings | BB.wBRWarn2St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module ambient over temperature. | Warnings | BB.wBRWarn2St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Module ambient under temperature. | Warnings | BB.wBRWarn2St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack over voltage. | Warnings | BB.wBRWarn3St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack over voltage String Voltage ≥ 1357.5V for 3 S TROUBLESHOOTING Stop discharging and check status | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack under voltage. | Warnings | BB.wBRWarn3St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack under voltage String Voltage ≤ 907.2V for 3 S TROUBLESHOOTING Stop charging and check status Report it to SDI representatives and investigate the battery module in detail. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Charge over current. | Warnings | BB.wBRWarn3St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN charge over current String Current ≥ 123A for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. power as ratio of Normal/Total Rack. Check the rack when available. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Charge over current 2nd. | Warnings | BB.wBRWarn3St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN charge over current 2nd TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Discharge over current. | Warnings | BB.wBRWarn3St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN discharge over current String Current ≤ -123A for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. power as ratio of Normal/Total Rack. Check the rack when available. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Discharge over current 2nd. | Warnings | BB.wBRWarn3St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN discharge over current 2nd TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Charge current limit fail. | Warnings | BB.wBRWarn3St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN charge current limit fail String Current ≥ Limit Spec for 5 S TROUBLESHOOTING Reduce the power as ratio of normal / total Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Discharge current limit fail. | Warnings | BB.wBRWarn3St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN discharge current limit fail String Current ≤ Limit Spec for 5 S TROUBLESHOOTING Reduce the power as ratio of normal / total Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Current sensor#2 charge over current. | Warnings | BB.wBRWarn3St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Current sensor#2 discharge over current. | Warnings | BB.wBRWarn3St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Sensor current difference. | Warnings | BB.wBRWarn3St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Recurring the charge current limit fail. | Warnings | BB.wBRWarn3St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Afe(module bms) hardware fail #4 | Warnings | BB.wBRWarn3St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn3St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn3St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn3St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Sensor voltage difference. | Warnings | BB.wBRWarn4St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN sensor voltage difference ¦Rack Sensor V - Rack Cell Sum V¦ ≥ 60.0V for 3 S TROUBLESHOOTING Check the rack when available. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Sensor sleep. | Warnings | BB.wBRWarn4St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN sensor sleep Sensor = Calibration Mode for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. 1. Check and replace Rack BMS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> sensor communication fail #1. | Warnings | BB.wBRWarn4St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> sensor comm. fail #1 Rx Timeout for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. Stop operating Check the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Rack <-> sensor communication fail #2. | Warnings | BB.wBRWarn4St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> sensor comm. fail #2 Rx Data Fail for 3 S TROUBLESHOOTING Stop operation and check the battery Sys.. Stop operating Check the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Additional protection fail. | Warnings | BB.wBRWarn4St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN additional protection fail (auxiliary protection operation) TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fan operation fail. | Warnings | BB.wBRWarn4St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fan operation fail TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Powerline wiring fail. | Warnings | BB.wBRWarn4St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN power line wiring fail TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn4St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Fuse or dc contactor sensing fail. | Warnings | BB.wBRWarn4St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fuse or dcsw sensing fail TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Current value stuck. | Warnings | BB.wBRWarn4St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN current stuck TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Current sensing wire open or short. | Warnings | BB.wBRWarn4St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN current sensing wire open or short. TROUBLESHOOTING [Alarm] Gives warning ahead of protection, at a lower level than protection is triggered at | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn4St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn4St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Reserved | Warnings | BB.wBRWarn4St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Permanent protection. | Warnings | BB.wBRWarn4St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W | Emergency stop protection. | Warnings | BB.wBRWarn4St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell over voltage. | Errors | BB.wBRFlt1St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell over voltage Max Cell Voltage ≥ 4.23V for 1 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell under voltage. | Errors | BB.wBRFlt1St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell under voltage Min Cell Voltage ≤ 2.7V for 3 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack cell voltage imbalance. | Errors | BB.wBRFlt1St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell voltage imbalance SOC ≥ 10% && Cell Voltage △ ≥ 300mV for 5 S TROUBLESHOOTING Stop operating, Check the failed Rack, If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell voltage hold. | Errors | BB.wBRFlt1St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell voltage hold Cell Voltage' = Cell Voltage for 3600 s TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. 1. Check Module BMS 2. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell over temperature. | Errors | BB.wBRFlt1St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell over temperature Max Cell Temperature > 65°C for 5s TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after Sys. has cooled down and after excluding the failed | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell under temperature. | Errors | BB.wBRFlt1St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell under temperature Max Cell Temperature < -21°C for 5s TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after Sys. has cooled down and after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell temperature imbalance. | Errors | BB.wBRFlt1St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN cell temperature imbalance cell temperature difference > 20°C per 30s TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt1St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Iterative Cell Balancing | Errors | BB.wBRFlt1St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN iterative cell balancing TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module open wire detection. | Errors | BB.wBRFlt1St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Recurring the cell over voltage. | Errors | BB.wBRFlt1St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Cell deviation fail | Errors | BB.wBRFlt1St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module cell voltage | Errors | BB.wBRFlt1St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt1St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt1St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt1St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module voltage difference. | Errors | BB.wBRFlt2St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN module voltage difference ¦Module Block V - Module Cell Sum V¦ ≥ 3.6V for 5 S TROUBLESHOOTING Stop operating Check the failed Module If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> module communication fail #1. | Errors | BB.wBRFlt2St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #1. RX Address ≠ Module Count for 30 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> module communication fail #2. | Errors | BB.wBRFlt2St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #2. Scan Fail for 30 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> module communication fail #3. | Errors | BB.wBRFlt2St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #3. TX Command ≠ RX Command for 30 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | All module sleep. | Errors | BB.wBRFlt2St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN all module sleep Min Cell Voltage ≤ 2.0V for 3600 TROUBLESHOOTING Stop operating Check the failed rack&module. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Afe(module bms) hardware fail #1 | Errors | BB.wBRFlt2St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN afe(module bms) hardware fail #1 ALRTRST Bit Set & Module ID = 0 for 20 times TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. 1. Check and replace Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module pcb over temperature. | Errors | BB.wBRFlt2St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN module mount check TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module pcb under temperature. | Errors | BB.wBRFlt2St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN module pcb under temperature. TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> module communication fail #4. | Errors | BB.wBRFlt2St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> module comm. fail #4. Data Fail for 30 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Afe(module bms) hardware fail #2 | Errors | BB.wBRFlt2St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN afe(module bms) hardware fail #2 ALRTTEMP Bit Set for 5 S (0x0055 Rack String Protection #2 sum. Bit 9) TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Afe(module bms) hardware fail #3 | Errors | BB.wBRFlt2St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN afe(module bms) hardware fail #3 ALRTHVUV or ALRTHVHDRM Bit Set for 5 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. 1. Check and replace Rack BMS. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fire detect condition #1. | Errors | BB.wBRFlt2St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fire detect condition #2. | Errors | BB.wBRFlt2St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fire detect condition #3. | Errors | BB.wBRFlt2St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module ambient over temperature. | Errors | BB.wBRFlt2St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Module ambient under temperature. | Errors | BB.wBRFlt2St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack over voltage. | Errors | BB.wBRFlt3St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack over voltage String Voltage ≥ 1370.5V for 1 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack under voltage. | Errors | BB.wBRFlt3St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack under voltage String Voltage ≤ 874.8V for 1 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Charge over current. | Errors | BB.wBRFlt3St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN charge over current String Current ≥ 130A for 1 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Charge over current 2nd. | Errors | BB.wBRFlt3St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN charge over current 2nd String Current ≥ 130A for 12 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Discharge over current. | Errors | BB.wBRFlt3St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN discharge over current String Current ≤ -130A for 1 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Discharge over current 2nd. | Errors | BB.wBRFlt3St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN discharge over current 2nd String Current ≤ -130A for 12 S TROUBLESHOOTING Stop operating Check the failed Rack. If necessary, restart the battery after excluding the failed Rack. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Charge current limit fail. | Errors | BB.wBRFlt3St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN charge current limit fail TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Discharge current limit fail. | Errors | BB.wBRFlt3St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN discharge current limit fail TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Current sensor#2 charge over current. | Errors | BB.wBRFlt3St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Current sensor#2 discharge over current. | Errors | BB.wBRFlt3St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Sensor current difference. | Errors | BB.wBRFlt3St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Recurring the charge current limit fail. | Errors | BB.wBRFlt3St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Afe(module bms) hardware fail #4 | Errors | BB.wBRFlt3St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt3St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt3St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt3St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Sensor voltage difference. | Errors | BB.wBRFlt4St | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN sensor voltage difference ¦Rack Sensor V - Rack Cell Sum V¦ ≥ 90.0V for 5 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Sensor sleep. | Errors | BB.wBRFlt4St | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN sensor sleep Sensor = Calibration Mode for 5 S (0x0057 Rack String Protection #4 sum. Bit 1) TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack 1. Check and replace Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> sensor communication fail #1. | Errors | BB.wBRFlt4St | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> sensor comm. fail #1 Rx Timeout for 5 S TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Rack <-> sensor communication fail #2. | Errors | BB.wBRFlt4St | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN rack <-> sensor comm. fail #2 Rx Data Fail for 5 S TROUBLESHOOTING Stop operating Check the failed Rack | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Additional protection fail. | Errors | BB.wBRFlt4St | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN additional protection fail (auxiliary protection operation) TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason [ | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fan operation fail. | Errors | BB.wBRFlt4St | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fan operation fail TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Powerline wiring fail. | Errors | BB.wBRFlt4St | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN power line wiring fail DC Close && P(+) Voltage ≤ 874.8V for 1 S (0x0057 Rack String Protection #4 sum. Bit 6) TROUBLESHOOTING Stop operating Check the failed Rack 1. Check the Powerline Wiring | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt4St | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Fuse or dc contactor sensing fail. | Errors | BB.wBRFlt4St | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN fuse or dcsw sensing fail TROUBLESHOOTING Stop operating Check the failed Rack If necessary, restart the battery after excluding the failed Rack 1. Check fuse status 2. Check DC Switch status 3. Check Rack BMS | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Current value stuck. | Errors | BB.wBRFlt4St | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN current stuck TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Current sensing wire open or short. | Errors | BB.wBRFlt4St | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN current sensing wire open or short. TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt4St | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt4St | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Reserved | Errors | BB.wBRFlt4St | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Permanent protection. | Errors | BB.wBRFlt4St | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Permanent protection TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A | Emergency stop protection. | Errors | BB.wBRFlt4St | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency stop protection TROUBLESHOOTING [Protection] Disconnects the charge/discharge path automatically for a safety reason | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0