## DiscreteAlarms
F ¦ Emergency push button 1 ¦ 513P1ESTOP1 | Errors | wHMI_Fault1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on P.EMS front door | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency push button external 2 ¦ 513S1ESTOP2 | Errors | wHMI_Fault1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency circuit ON TROUBLESHOOTING Check the status of the container. Reset the emergency relay on the container door (PCS room) | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Insulation Control Device C-BESSHD1 Trip ¦ | Errors | wHMI_Fault1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Insulation losses occured TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Surge suppressor trip ¦ 001F1 | Errors | wHMI_Fault1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor intervention TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Main circuit breaker ¦ 003F2 | Errors | wHMI_Fault1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc Communication Equipment ¦ 301F1 | Errors | wHMI_Fault1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Power supply 24Vdc Safety PLC cards ¦ 301F2 | Errors | wHMI_Fault1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ PCS door open ¦ 527S1/527S2 | Errors | wHMI_Fault1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ AC door open ¦ 527S5/527S6 | Errors | wHMI_Fault1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PCS room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Emergency State ¦ | Errors | wHMI_Fault1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency State Activated TROUBLESHOOTING Chech Emergency Alarm/Fault or reset Emergency Chain | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Master Profinet communication Error ¦ | Errors | wHMI_Fault2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Master Profinet comm. fault with PEMS Core TROUBLESHOOTING Check comm. status or connection | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Maximum Temperature Alarm PCS room¦ | Errors | wHMI_Fault2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
F ¦ Spare | Errors | wHMI_Fault2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply C-BESSHD1 ¦ 013F2 | Errors | wHMI_Alarm1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply C-BESSHD2 ¦ 013F3 | Errors | wHMI_Alarm1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Main circuit breaker open UPS ¦ 101F2 | Errors | wHMI_Alarm1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Surge suppressor UPS trip ¦ 101F3 | Errors | wHMI_Alarm1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Surge suppressor intervention TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PS unit 1 24Vdc open ¦ 107F2+107T1 | Errors | wHMI_Alarm1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power Supply UPS PS unit 2 24Vdc open ¦ 107F3+107T2 | Errors | wHMI_Alarm1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply UPS C-BESSHD1 open¦ 107F4 | Errors | wHMI_Alarm1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply UPS C-BESSHD2 open¦ 107F5 | Errors | wHMI_Alarm1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc digital PLC cards ¦ 301F3 | Errors | wHMI_Alarm1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc analog PLC cards ¦ 301F4 | Errors | wHMI_Alarm1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PLC IO internal ¦ 301F5 | Errors | wHMI_Alarm1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PLC IO external ¦ 301F6 | Errors | wHMI_Alarm1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Circuit breaker trip TROUBLESHOOTING Check the status of the circuit breaker and attempt a reclosure | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply 24Vdc PCS Signals ¦ 301F7 | Errors | wHMI_Alarm1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply fan 1 ¦ 011F1 | Errors | wHMI_Alarm2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Power supply fan 2 ¦ 011F2 | Errors | wHMI_Alarm2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Internal intake pressure switch ¦ | Errors | wHMI_Alarm2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ External intake pressure switch ¦ | Errors | wHMI_Alarm2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Irresponsive fan 1 ¦ | Errors | wHMI_Alarm2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Irresponsive fan 2 ¦ | Errors | wHMI_Alarm2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ EH05HD1 Profinet communication Error ¦ with core? | Errors | wHMI_Alarm3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ EH05HD2 Profinet communication Error ¦ with core? | Errors | wHMI_Alarm3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL1,C-BESSHD1 CAN communication Error ¦ | Errors | wHMI_Alarm3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL2,C-BESSHD1 CAN communication Error ¦ | Errors | wHMI_Alarm3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL1,C-BESSHD2 CAN communication Error ¦ | Errors | wHMI_Alarm3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ CL2,C-BESSHD2 CAN communication Error ¦ | Errors | wHMI_Alarm3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 1 in Alarm ¦ | Errors | wHMI_Alarm3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 1 in Fault State TROUBLESHOOTING Check State Machine 1 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 2 in Alarm ¦ | Errors | wHMI_Alarm3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 2 in Fault State TROUBLESHOOTING Check State Machine 2 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 3 in Alarm ¦ | Errors | wHMI_Alarm3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 3 in Fault State TROUBLESHOOTING Check State Machine 3 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ State Machine 4 in Alarm ¦ | Errors | wHMI_Alarm3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN State Machine 4 in Fault State TROUBLESHOOTING Check State Machine 4 Alarms/Faults | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
A ¦ Spare | Errors | wHMI_Alarm3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor C-BESSHD1 shot ¦ | Errors | wHMI_Alarm3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor C-BESSHD2 shot ¦ | Errors | wHMI_Alarm3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Emergency State Activated TROUBLESHOOTING Chech Emergency Alarm/Fault or reset Emergency Chain | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 1 high temperature ¦ 561B1 | Warnings | wHMI_Warning1 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 1 low temperature ¦ 561B1 | Warnings | wHMI_Warning1 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 1 temperature read fail ¦ 561B1 | Warnings | wHMI_Warning1 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 1 high humidity ¦ 561B1 | Warnings | wHMI_Warning1 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 1 low humidity ¦ 561B1 | Warnings | wHMI_Warning1 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 1 humidity read fail ¦ 561B1 | Warnings | wHMI_Warning1 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 2 high temperature ¦ 561B2 | Warnings | wHMI_Warning1 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized high temperature inside the C-BESSHD room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 2 low temperature ¦ 561B2 | Warnings | wHMI_Warning1 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Localized low temperature inside the Battery Room TROUBLESHOOTING Check the status of the Battery Room, of the HVAC units and check the temperature set point | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 2 temperature read fail ¦ 561B2 | Warnings | wHMI_Warning1 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 2 high humidity ¦ 561B2 | Warnings | wHMI_Warning1 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 2 low humidity ¦ 561B2 | Warnings | wHMI_Warning1 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD room sensor 2 humidity read fail ¦ 561B2 | Warnings | wHMI_Warning1 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING Check the status of the C-BESSHD Room Temperature/Humidity sensor | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning1 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ P.EMS or fans door open ¦ 527S3/527S4 | Warnings | wHMI_Warning2 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN PEMS or fans room service door has been opened TROUBLESHOOTING Check presence of non authorized people | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Insulation Control Device C-BESSHD1 Alarm ¦ | Warnings | wHMI_Warning2 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Insulation losses occured TROUBLESHOOTING Check the status of the container. | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning2 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD1 CL1 Synch Warning ¦ | Warnings | wHMI_Warning3 | 0 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD1 CL2 Synch Warning ¦ | Warnings | wHMI_Warning3 | 1 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD2 CL1 Synch Warning ¦ | Warnings | wHMI_Warning3 | 2 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD2 CL2 Synch Warning ¦ | Warnings | wHMI_Warning3 | 3 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD Synch Warning: No Master¦ | Warnings | wHMI_Warning3 | 4 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD Synch Warning: More than one Master¦ | Warnings | wHMI_Warning3 | 5 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD Synch Warning: Slave Error¦ | Warnings | wHMI_Warning3 | 6 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ C-BESSHD Synch Warning: No Sync Active¦ | Warnings | wHMI_Warning3 | 7 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN C-BESSHD Master and Slave Synchronization Error TROUBLESHOOTING Check the status of the C-BESSHD in the Container | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ HVAC unit not enabled ¦ | Warnings | wHMI_Warning3 | 8 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN HVAC unit not Enabled TROUBLESHOOTING Check the status of the HVAC, in case enable it | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Both HVAC compressor not enabled ¦ | Warnings | wHMI_Warning3 | 9 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN Both HVAC compressor Disabled TROUBLESHOOTING Check the status of the HVAC, in case enable it | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 10 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 11 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 12 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Spare | Warnings | wHMI_Warning3 | 13 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False |  | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor C-BESSHD1 open ¦ | Warnings | wHMI_Warning3 | 14 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0
W ¦ Surge Suppressor C-BESSHD2 open ¦ | Warnings | wHMI_Warning3 | 15 | On rising edge | <No value> | 0 | <No value> | 0 | <No value> | 0 | False | ORIGIN TROUBLESHOOTING | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | <No value> | False | 0 | 0 | 0